# Watchdog Energy Management Software Testing Checklist

Customer acceptance and commissioning test plan
Software version 4.2.0

| Site or customer |  | Test date |  |
| --- | --- | --- | --- |
| Main PC name |  | Main PC IP |  |
| Tester |  | Build or release | V4.2.0 |
| License capacity |  | Meter count |  |

# How to use this checklist

Use a test laptop or an approved commissioning period. Complete the steps in order. Tick a box only when the expected result is confirmed. Record evidence or a fault reference in the notes column. Never test destructive actions on the only production database.

Result marks  ☐ Not tested    ☐ Pass    ☐ Fail    ☐ Not applicable

# 1 Test preparation

Objective  Protect customer data and prepare evidence before changing configuration.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 1 | Download the V4.2.0 installer or ZIP from the official GitHub release. Expected result: The file name shows version 4.2.0 and the download completes. |  |
| ☐ | 2 | Use a dedicated test PC or make a verified Watchdog backup before testing an existing site. Expected result: A dated backup exists in a separate safe location. |  |
| ☐ | 3 | Record the main PC name, IPv4 address, Windows version and network connection above. Expected result: The test record identifies the exact computer and network. |  |
| ☐ | 4 | Collect approved meter maps and communication settings from the meter, PLC, DDC or gateway manufacturer. Expected result: Register addresses, units, data type, word order, scale and communication parameters are available. |  |
| ☐ | 5 | Prepare safe demonstration shops, meters and email addresses. Expected result: No private credentials or real customer email recipients are used during initial testing. |  |
| ☐ | 6 | Confirm the PC date, time and time zone. Expected result: Windows shows the correct local date, time and time zone. |  |

# 2 Installation and startup

Objective  Confirm that Watchdog installs, starts and survives normal Windows operation.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 7 | Run the Watchdog V4.2.0 Windows installer as Administrator. Expected result: Installation completes without an error and creates the desktop shortcut. |  |
| ☐ | 8 | Open Windows Services and locate Watchdog Energy Management Server. Expected result: The service exists, is Running and uses Automatic startup. |  |
| ☐ | 9 | Double-click the Watchdog Energy Management desktop shortcut. Expected result: The browser opens the Watchdog sign-in or dashboard at http://localhost:5080. |  |
| ☐ | 10 | Open Main and select About Watchdog. Expected result: The About window displays version 4.2.0. |  |
| ☐ | 11 | Open Main and select Help. Expected result: The bundled customer manual opens in a new browser tab and can be downloaded. |  |
| ☐ | 12 | Lock Windows with Win+L for at least five minutes, sign back in and refresh Watchdog. Expected result: The service and dashboard remain available. |  |
| ☐ | 13 | Restart Windows and wait for startup to finish. Expected result: The Watchdog service starts automatically and the shortcut opens the application. |  |

# 3 License and administrator access

Objective  Confirm licensing limits and protected administration functions.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 14 | Open Settings and select License. Expected result: The page displays the Installation ID, license status, edition and active-meter allowance. |  |
| ☐ | 15 | If testing a commercial license, import the signed license issued for this Installation ID. Expected result: The license validates and the correct customer, capacity and expiry information appear. |  |
| ☐ | 16 | Confirm that the private license signing key is not present on the customer PC. Expected result: Only the signed license file is available to Watchdog. |  |
| ☐ | 17 | Sign in with an Administrator test account. Expected result: Settings pages and administrator controls become available. |  |
| ☐ | 18 | Sign out and try a lower-access test account. Expected result: The user sees only pages and actions allowed for that access level. |  |

# 4 Users and permissions

Objective  Verify that accounts can be created and that each access level is enforced.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 19 | Open Settings and select Users and Access. Expected result: The account list and create-user form load. |  |
| ☐ | 20 | Create one temporary test user with a unique username, information email and strong temporary password. Expected result: The user appears in the list and no password is displayed. |  |
| ☐ | 21 | Assign Viewer and sign in as that user. Expected result: The user can view permitted monitoring information but cannot change administrator configuration. |  |
| ☐ | 22 | Repeat permission checks for Operator and Billing Manager where those roles will be used. Expected result: Operational and billing actions match the configured role descriptions. |  |
| ☐ | 23 | Return to Administrator and delete the temporary account after testing. Expected result: The test account is removed while the signed-in administrator account remains protected. |  |

# 5 Shops customers and tenants

Objective  Confirm that billing identities and contact information are correct and editable.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 24 | Open Settings and select Shops. Expected result: The shop setup page loads. |  |
| ☐ | 25 | Create a demonstration shop with shop number, name, tenant, location and test email address. Expected result: The shop is saved and appears in the configured shop list. |  |
| ☐ | 26 | Edit the shop name, tenant or email and save. Expected result: The updated information appears after refresh. |  |
| ☐ | 27 | Confirm the email address uses an approved test inbox. Expected result: Automatic invoice tests cannot reach a real customer accidentally. |  |
| ☐ | 28 | Archive or deactivate the demonstration shop if it will not be used later. Expected result: The shop no longer appears as an active assignment while retained records remain consistent. |  |

# 6 System features

Objective  Verify optional water features without changing electricity behavior.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 29 | Open Settings and select System features. Expected result: The Water metering and billing switch is visible to an Administrator. |  |
| ☐ | 30 | Enable Water metering and billing and save. Expected result: Water appears in the Main menu and water meter options become available. |  |
| ☐ | 31 | Open Water and confirm the blue monitoring design and search banner. Expected result: The page loads and displays only water meters. |  |
| ☐ | 32 | Disable Water temporarily and save. Expected result: The Water menu and water setup options are hidden; electricity pages still work. |  |
| ☐ | 33 | Restore the feature setting required for the site. Expected result: The final menu matches the customer's installed utilities. |  |

# 7 Controller communication

Objective  Prove each configured communication path before commissioning meters.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 34 | Open Settings and select Controller setup. Expected result: The controller list loads with protocol, condition and action buttons. |  |
| ☐ | 35 | Create or edit a Modbus RTU controller using the approved COM port, baud, parity, data bits, stop bits, timeout and retries. Expected result: The saved values match the approved serial settings. |  |
| ☐ | 36 | Test the Modbus RTU controller with the field cable connected. Expected result: The controller reports a successful response and updates Last success. |  |
| ☐ | 37 | Create or edit a Modbus TCP controller using the approved IP address, TCP port and unit address. Expected result: The saved network values match the gateway or device configuration. |  |
| ☐ | 38 | Test the Modbus TCP controller. Expected result: The controller is reachable and returns a valid Modbus response. |  |
| ☐ | 39 | For BACnet IP, select the correct local interface, target device IP, UDP port and device instance. Expected result: The controller identifies the intended BACnet device. |  |
| ☐ | 40 | Run BACnet discovery or direct device test and browse objects if allowed. Expected result: The intended device responds and the required objects are visible. |  |
| ☐ | 41 | Disconnect one test communication path briefly and reconnect it. Expected result: Watchdog shows a failure or stale state, then recovers without restarting after communication returns. |  |

# 8 Meter setup and commissioning

Objective  Confirm that every meter points to the correct field value and billing customer.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 42 | Open a controller and create only the required meter channels, up to the supported 45 channels per controller. Expected result: Channel count and addresses match the approved register or point schedule. |  |
| ☐ | 43 | Create an electricity meter and enter the meter name, physical serial number, utility type, Grid or Generator source, shop and communication mapping. Expected result: The meter saves under the selected source and shop. |  |
| ☐ | 44 | For Modbus, confirm start register, data type, word order and scale against the manufacturer's map. Expected result: A known raw value converts to the expected engineering value. |  |
| ☐ | 45 | For BACnet, configure the object type, object instance, Present Value property, unit, scale and offset. Expected result: A test read matches the physical meter and only a confirmed cumulative energy point is enabled for billing. |  |
| ☐ | 46 | Create a water meter through the approved M Bus to Modbus gateway mapping when Water is enabled. Expected result: The meter reports cumulative volume in m3 and appears only on Water. |  |
| ☐ | 47 | Select Commissioned and active only after the physical value has been verified. Expected result: The meter begins polling and counts toward license capacity. |  |
| ☐ | 48 | Use View meter and compare the Watchdog accumulated reading with the physical meter display. Expected result: The values match within the approved tolerance. |  |
| ☐ | 49 | Verify the meter appears automatically on Dashboard and on Grid, Generator or Water as assigned. Expected result: No meter appears on the wrong utility or power-source page. |  |

# 9 Monitoring search graphs and alarms

Objective  Verify everyday monitoring, automatic refresh and investigation tools.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 50 | Observe the Dashboard through at least two polling intervals. Expected result: Readings, last-reading times and communication states refresh without creating another polling service. |  |
| ☐ | 51 | Search Grid or Generator by meter ID, meter name, tenant and location. Expected result: Only matching meters from the selected power source are shown. |  |
| ☐ | 52 | Search Water by meter or customer information. Expected result: Only matching water meters are shown. |  |
| ☐ | 53 | Search for a value that does not exist. Expected result: The page displays No matching meter was found. |  |
| ☐ | 54 | Open a meter from Dashboard, Grid, Generator or Water. Expected result: The same meter detail page opens from every entry point. |  |
| ☐ | 55 | Review Per Day, Per Month and Per Year charts and move the pointer over bars. Expected result: Tooltips show the period, consumption and cost using the active tariff. |  |
| ☐ | 56 | Review communication states including Connected, Partial data, Stale, Failed, Disabled and Not commissioned where practical. Expected result: Each state is clear and consistent with the simulated or real condition. |  |
| ☐ | 57 | Restore every disconnected test device. Expected result: All required production meters return to a healthy state before billing tests. |  |

# 10 Tariffs and monthly billing schedule

Objective  Verify meter-specific pricing and automatic publication settings.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 58 | Open Main, select Operations and go to Tariffs and invoice day. Expected result: The tariff and monthly publication controls load. |  |
| ☐ | 59 | Select one demonstration meter, enter a test tariff and ISO currency, then save. Expected result: The tariff becomes active immediately for that meter only. |  |
| ☐ | 60 | Set a different tariff for a second demonstration meter. Expected result: Each meter retains its own tariff and currency. |  |
| ☐ | 61 | Select the monthly publication day from day 1 through day 7 and enter payment due days. Expected result: The current schedule and next publication date are displayed. |  |
| ☐ | 62 | Confirm that all active billable meters have valid readings before the period closes. Expected result: Each meter has accepted opening and closing cumulative readings. |  |
| ☐ | 63 | Do not change the Windows clock on a production PC to force billing. Expected result: The test uses a prepared test database, approved test machine or waits for the scheduled date. |  |
| ☐ | 64 | Allow Watchdog to run across the scheduled publication time on the test system. Expected result: One finalized invoice is published for each eligible meter for the completed period. |  |

# 11 Invoice validation

Objective  Confirm every published invoice is accurate, readable and traceable.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 65 | Open Main and select Published invoices. Expected result: The archive shows the newly published invoices. |  |
| ☐ | 66 | Search by day, month, year, shop, tenant, meter or invoice number. Expected result: The archive returns only matching invoices. |  |
| ☐ | 67 | Open one electricity invoice and compare its opening reading, closing reading and consumption. Expected result: Consumption equals closing reading minus opening reading. |  |
| ☐ | 68 | Recalculate usage charge using consumption multiplied by the meter tariff. Expected result: The calculated amount matches the invoice. |  |
| ☐ | 69 | Check currency, charges, tax, discount, invoice date and due date. Expected result: Every value matches the approved configuration. |  |
| ☐ | 70 | Open one water invoice if Water is enabled. Expected result: The invoice uses m3 and the water meter tariff. |  |
| ☐ | 71 | Select Download PDF and open the file. Expected result: The PDF is readable and shows the correct customer, meter, period and totals. |  |
| ☐ | 72 | Use Print preview without printing. Expected result: The invoice fits the page and no content is clipped. |  |
| ☐ | 73 | Record a test payment if payment processing is in scope. Expected result: The status and outstanding balance update correctly. |  |

# 12 Invoice email

Objective  Prove manual and automatic PDF delivery using only approved test recipients.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 74 | Open Settings and select Invoice email. Expected result: SMTP configuration and the standard customer message are visible. |  |
| ☐ | 75 | Enter the test SMTP host, port, TLS setting, username, app password, sender and standard message, then save. Expected result: Settings save and the password is retained encrypted for this Windows installation. |  |
| ☐ | 76 | Send a test email to an approved test inbox. Expected result: The message arrives from the configured sender. |  |
| ☐ | 77 | Send one invoice PDF manually from its detail page. Expected result: The recipient receives the correct invoice attachment and message. |  |
| ☐ | 78 | Enable the global PDF email switch and automatic invoice delivery on the test system. Expected result: Newly published invoices are queued for automatic delivery. |  |
| ☐ | 79 | Complete an approved scheduled-publication test. Expected result: Each eligible test customer receives only their own invoice PDF. |  |
| ☐ | 80 | Disable automatic delivery after testing unless the customer has approved production email. Expected result: Manual or automatic behavior matches the final customer decision. |  |

# 13 Reports readings and audit

Objective  Confirm that operational evidence can be found and exported.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 81 | Open Operations and expand Reading history. Expected result: Recent readings show meter, time, value, source, quality and billing-use information. |  |
| ☐ | 82 | Select Export readings CSV and open the file in a spreadsheet application. Expected result: The CSV contains readable columns and expected test readings. |  |
| ☐ | 83 | Use meter graphs and invoice PDF or archive as the available customer reports. Expected result: Daily, monthly and yearly usage plus financial records are accessible. |  |
| ☐ | 84 | Open Settings and select Audit trail. Expected result: Recent configuration, tariff, billing, backup, user and deletion actions identify user, time and result. |  |
| ☐ | 85 | Compare one audit entry with the action performed during this checklist. Expected result: The entry accurately describes the tested change. |  |

# 14 Backup restore and data protection

Objective  Prove that configuration and billing data can be recovered.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 86 | Open Operations and go to Backup and restore. Expected result: The Administrator backup section loads. |  |
| ☐ | 87 | Select Create new backup. Expected result: A new dated backup appears with a reasonable nonzero size. |  |
| ☐ | 88 | Copy the backup to the customer's approved separate storage location. Expected result: A second copy exists outside the Watchdog data folder. |  |
| ☐ | 89 | On a non-production test copy only, select the backup and run restore. Expected result: Watchdog restores the database and restarts or reloads as designed. |  |
| ☐ | 90 | Verify shops, controllers, meters, readings, tariffs, users and invoices after restore. Expected result: The restored test system matches the saved backup. |  |
| ☐ | 91 | Create a final pre-commissioning backup. Expected result: A clearly dated recovery point is available before launch. |  |

# 15 LAN browser access

Objective  Confirm that authorized users can view the same server and database from the customer network.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 92 | Confirm the main PC uses a stable IPv4 address and Watchdog listens on TCP port 5080. Expected result: http://localhost:5080 works on the main PC. |  |
| ☐ | 93 | Confirm the Windows Firewall inbound TCP 5080 rule is enabled for the required private network profile. Expected result: The firewall permits approved LAN clients without exposing unrelated ports. |  |
| ☐ | 94 | Connect a second computer or mobile device to the same authorized LAN or Wi Fi. Expected result: The client receives a compatible IP address and can reach the main PC. |  |
| ☐ | 95 | Open http://MAIN-PC-IP:5080 on the second device. Expected result: The Watchdog sign-in page opens from the main server. |  |
| ☐ | 96 | Sign in with a Viewer test account and compare readings with the main PC. Expected result: Both browsers show the same meters, readings, invoices and database information. |  |
| ☐ | 97 | Close the second browser. Expected result: Meter polling on the main PC continues without interruption. |  |

# 16 Reliability and final acceptance

Objective  Confirm recovery from normal interruptions and record the release decision.

| Check | Step | Test action and expected result | Notes or evidence |
| --- | --- | --- | --- |
| ☐ | 98 | Run Watchdog continuously for the agreed pilot period while monitoring logs and communication. Expected result: No unexplained service stop, duplicate polling or data corruption occurs. |  |
| ☐ | 99 | Disconnect and reconnect Ethernet or Wi Fi on the main PC without changing field wiring. Expected result: LAN clients lose access temporarily and recover when networking returns; local polling follows its configured interface. |  |
| ☐ | 100 | Restart the Watchdog Windows service during an approved test window. Expected result: The application returns on port 5080 and resumes scheduled background work. |  |
| ☐ | 101 | Confirm adequate free disk space and review the Watchdog Logs folder. Expected result: Disk space is acceptable and no unresolved critical error remains. |  |
| ☐ | 102 | Compare selected final readings with physical meters and verify one complete billing cycle. Expected result: Reading accuracy and invoice calculations are accepted by the responsible customer representative. |  |
| ☐ | 103 | Resolve or formally accept every failed checklist item. Expected result: No unexplained failure remains open at production launch. |  |

# Final test summary

| Overall result | ☐ Pass ☐ Conditional pass ☐ Fail |
| --- | --- |
| Open fault references |  |
| Approved meter count |  |
| Approved utilities | ☐ Electricity Grid ☐ Electricity Generator ☐ Water |
| Customer representative |  |
| Tester signature |  |
| Acceptance date |  |

Launch rule  Use Watchdog for production billing only after communication values, tariffs, invoice calculations, backups, user permissions and recovery behavior have passed or have documented customer acceptance.